## OCP2.1(B)
LCCC Wind Commissioning Guidance Tracker - 80% of Installed Capacity Operational Condition Precedent 2.1 (B)
Project Name:
Installed Capacity Estimate (MW)
Number of WTGs
WTG Type (model)
WTG Capacity (each)
Total Capacity (MW)
Connected to
Section 4: Commissioning Evidence | Further Guidance/Explanation | Document Name / Reference | LCCC Comment(s) | Generator Comment(s) | Status [DATE]
A. Evidence of successful commissioning of the Wind Turbine Generators (WTGs) comprising in aggregate not less than 80% of the Installed Capacity Estimate of the Facility in the form either a) or b), followed by the mandatory submission of c);
a) Dated, valid Take Over Certificates (TOCs) for each of the WTGs comprising in aggregate not less than 80% of the Installed Capacity Estimate of the Facility (see Section 4.1 D on how to perform the 80% calculation). The TOC must be supplemented with Supporting Information of the technical requirements and tests undertaken to enable the issuance of respective certificate(s).
Or alternatively;
b) Dated, valid Commissioning Completion Certificates (CCCs) including appropriate certification(s) on HV commissioning, start-up commissioning and energisation readiness for each of the WTGs comprising in aggregate not less than 80% of the Installed Capacity Estimate of the Facility. The CCCs must be supplemented with Supporting Information of the technical requirements and commissioning tests undertaken to be able to issue the respective certificate. | See Wind Commissioning Guidance to read further on Supporting Information
In addition to either of the above,
c) the submissions must be accompanied by a Directors’ Certificate (DC) certifying that the WTGs installed and commissioned are ready for commercial operation. This may be submitted as a single DC or included as part of a consolidated 2.1B Directors’ Certificate, as detailed in Section 7.
B. Evidence of successful commissioning of the Electrical Balance of Plant (EBOP) system required to export energy of not less than the 80% of the Installed Capacity Estimate of the Facility in the form either a) or b), followed by the mandatory submission of c);
a) Dated, valid TOCs with respect to each contractor supplying and/or installing parts of the main components forming the EBOP (array power cables, transmission power cables, overhead lines, switchgear, transformers, power quality compliance equipment, reactive compensation equipment, Facility Metering Equipment, onshore / offshore substations). The TOC must be supplemented with Supporting Information of the technical requirements and tests undertaken to enable the issuance of the respective certificate(s) | See Wind Commissioning Guidance to read further on Supporting Information
Or alternatively;
b) Supporting Information of the technical requirements and commissioning tests performed on each of the main components forming the EBOP. The list should include the type of test performed, date of the test, results of the test in binary fashion (pass/fail) and a summary of any anomalies that occurred during the test.
In addition to either of the above,
c) the submission should be accompanied by a Directors’ Certificate (DC), certifying the EBOP is ready for commercial operation. This may be submitted as a stand-alone DC or included as part of a consolidated 2.1B Directors’ Certificate, as explained in Section 7.
C. There are three necessary components to establish that a sufficient number of turbines have been commissioned to meet the 80% threshold:
a) Calculation of the equivalent net capacity of turbines to establish whether enough turbines have been commissioned to meet the 80% threshold. This determines the number of WTGs that need to have the TOCs / CCCs issued as referred to in point 4.1A. To establish the number of WTG required to achieve the 80% Installed Capacity Estimate threshold, the gross WTG capacity must be assessed on a net capacity basis. When assessing whether sufficient TOCs / CCCs have issued as referred to in point 4.1A, LCCC will assume that total electrical losses for the project are 2%, as per the example below | A full Electrical Losses study will need to be provided to justify the use of a value lower than 2%.
b) Type certificate of the WTGs issued by the turbine manufacturer indicating the nameplate capacity7 of the WTG, with the incorporation of power modes/operating modes reflected on the type certificate itself or supplementary data sheet.
c) Director's Certificate clearly identifying the corresponding specification of turbine and operating mode that has been installed and the consequent rated output power of each turbine. In cases where only one turbine specification is incorporated in the type certificate/data sheet, the Generator will still need to provide a Director’s Certificate certifying accordingly. This may be submitted as a stand-alone DC or included as part of a consolidated 2.1B Directors’ Certificate, as explained in Section 7.
D. In order to gain a full understanding of the Facility (and validating the EBOP) which is progressing through OCP 2.1 (B) the Generator must provide:
a) Facility layout, containing a scale drawing of the Facility, in high resolution, with the following clearly shown (see right) | • Layout of the WTGs including the locations of the main components (as referenced in 4.1B) • Depiction of the Facility boundary (asset ownership boundary) • General arrangement of the onshore/offshore substation(s) • All power cables from WTGs to the Facility boundary • Location of Facility Metering Equipment
b) Single line diagram indicating the main components (as referenced in 4.1B) and their locations.
Section 5: Facility Commissioning Evidence
A. Facilities that are distribution connected must provide the G99 test certificate | (except where already accepted under an alternative Operational Condition Precedent and the CP Response Notice confirms that the Generator has fulfilled the Operational Condition Precedent)
B. All Facilities connected to the Transmission System, all ‘Large’ distribution connected projects as defined in the Grid Code, and all ‘Medium’ distribution connected projects as defined in the Grid Code that are subject to a Bilateral Agreement9, must provide an ION/ION (B) | (except where already accepted under an alternative Operational Condition Precedent and the CP Response Notice confirms that the Generator has fulfilled the Operational Condition Precedent).
C. All Facilities must Perform a “Whole Facility” test10 and provide historic metered output data to demonstrate that the commissioned WTGs and all the associated Facility equipment are effectively operating together (rather than in isolation), while indirectly supporting SCADA system functionality, as described in a) and b) below. | (except those >100MW that are able to separately demonstrate the removal of the 70% ION/ION (B) restrictions)
a) The Whole Facility Test ("WFT") All turbines being evidenced for the purpose of the OCP submission must, in a 30-min WFT: • demonstrate 100% of the WTG (every WTG included as part of 4.1A) have generated in every 10-minute intervals (where smaller intervals data sets will be adjusted accordingly to assess the same requirements). | See Wind Commissioning Guidance to read a simplified example of a SCADA whole Facility test output, demonstrating successful WTG generation (to be clear, any generation in that 10-minute period would signify a pass of this condition).
b) Historic metered output data. LCCC will review the provided historic metered output data and assess whether the total generation outputs are broadly expected and aligned with local weather conditions and the timing of the installation of your WTGs. If your SCADA output provides wind speed data, please provide this also.
D. All Facilities >100MW can, instead of the WFT, provide:
a) an Interim Operational Notification (ION), or for Offshore wind projects an ION (B), together with the Schedule of Unresolved Issues with the previously applied 70% restrictions (hold-off points) lifted. | The Schedule of Unresolved Issues, which identifies the application of the 70% restriction when first issued, is often presented as a working document that includes tracked changes and strike-through text as issues are resolved and restrictions are lifted; subsequently the Schedule can often look like a draft document.
Please provide one of the following for verifying authenticity, providing it is clear the restrictions are lifted
b) ION or ION (B) certificate and Schedule showing that all applicable restrictions are lifted.
c) The email from National Grid attaching the ION or ION (B) certificate and the latest Schedule of Unresolved Issues. The email should be copied and pasted by the original recipient as an attachment and should not be provided in a ‘forwarded’ form to the LCCC. It should also not be a pdf or printed form of the email. LCCC need to be able to verify that the attachment belongs to the National Grid email and comes from a National Grid email address.
d) ION or ION (B) certificate and Schedule of Unresolved Issues certified by NGESO as being correct and up to date by a person with appropriate authority.
E. The submission must be accompanied by a Directors’ Certificate (DC), certifying that in the immediate and foreseeable future there is no expected or anticipated risk of failure that should be brought to the CfD Counterparty(‘s) attention, nothing to stop exporting at no less than 80% of the Installed Capacity Estimate and the Facility is fit for commercial operation certifying the EBOP is ready for commercial operation. This may be submitted as a stand-alone DC or included as part of a consolidated 2.1B Directors’ Certificate, as explained in Section 7.
Section 6: Phased Projects (if applicable)
A. Provide a procedural document to demonstrate that a robust and consistent procedure is followed to meet the Information and Monitoring System Obligation.
Section 7: Directors' Certificate Requirements
For convenience, a consolidated Directors’ Certificate template is attached at Annex A of the Wind Commissioning guidance. | See Annex A template or Wind Commissioning Guidance for further information.
Other
2.1B OCP Notice

## CCCs.TOCs
WTG CCCs/TOCs (Document Name / Reference) | Date received | WTG | Dated | Accepted (Y/N) | Required number of CCCs | Received to date
|  |  |  | Y | 0 | 0
N

## Data
Connected to | Status
Transmission System | Submitted
Distribution Network (Embedded) | Satisfactory
Private-Wire | Outstanding